## eff_data_2020
Date | No of machine on Day | No of machine on Night | YOC Gas Nom. (Gbtu) | PCI Gas Nom. (Gbtu) | YOC Gas Nom. (GJ) | PCI Gas Nom. (GJ) | Total Gas Nom (GJ) | Actual MW (MWh) | Acutal gas used (GJ) | Station Work (MWh) | Simulated Gas used (GJ) | Simulated Station Work (MWh) | Totol Cost (HKD$) | Actual (GJ/MWh) | Simulated (GJ/MWh) | % drop in (GJ/MWh)
2021-02-18 | 6 | 3 | 185 | 128 | 195185.36 | 135047.168 | 330232.528 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-02-19 | 6 | 3 | 185 | 128 | 195185.36 | 135047.168 | 330232.528 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-02-20 | 6 | 3 | 185 | 110 | 195185.36 | 116056.16 | 311241.52 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-02-21 | 6 | 3 | 185 | 110 | 195185.36 | 116056.16 | 311241.52 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-02-22 | 6 | 3 | 181 | 99 | 190965.136 | 104450.544 | 295415.68 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-02-23 | 6 | 4 | 115 | 135 | 121331.44 | 142432.56 | 263764 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-02-24 | 6 | 4 | 140 | 152 | 147707.84 | 160368.512 | 308076.352 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-02-25 | 6 | 3 | 125 | 149 | 131882 | 157203.344 | 289085.344 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-03-17 | 7 | 3 | 160 | 113 | 168808.96 | 119221.328 | 288030.288 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-03-18 | 7 | 3 | 170 | 117 | 179359.52 | 123441.552 | 302801.072 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-03-19 | 7 | 3 | 170 | 121 | 179359.52 | 127661.776 | 307021.296 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-03-20 | 7 | 3 | 170 | 121 | 179359.52 | 127661.776 | 307021.296 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-03-21 | 7 | 3 | 160 | 113 | 168808.96 | 119221.328 | 288030.288 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-03-22 | 7 | 3 | 170 | 106 | 179359.52 | 111835.936 | 291195.456 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-03-23 | 7 | 3 | 160 | 121 | 168808.96 | 127661.776 | 296470.736 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-03-24 | 7 | 3 | 185 | 131 | 195185.36 | 138212.336 | 333397.696 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-04-14 | 6 | 2 | 100 | 174 | 105505.6 | 183579.744 | 289085.344 | 29626.4108 | 235873.2315 | 69.3333 |  |  |  | 7.9616 | #DIV/0! | #DIV/0!
2021-04-15 | 5 | 2 | 70 | 173 | 73853.92 | 182524.688 | 256378.608 | 24122.5649 | 197313.7068 | 78.2222 |  |  |  | 8.1796 | #DIV/0! | #DIV/0!
2021-04-16 | 5 | 2 | 90 | 173 | 94955.04 | 182524.688 | 277479.728 | 25413.462 | 205356.2117 | 67.5556 |  |  |  | 8.0806 | #DIV/0! | #DIV/0!
2021-04-17 | 5 | 2 | 110 | 173 | 116056.16 | 182524.688 | 298580.848 | 30511.3869 | 233139.8005 | 71.1111 |  |  |  | 7.6411 | #DIV/0! | #DIV/0!
2021-04-18 | 6 | 2 | 110 | 173 | 116056.16 | 182524.688 | 298580.848 | 29611.8815 | 228030.3728 | 69.3333 |  |  |  | 7.7006 | #DIV/0! | #DIV/0!
2021-04-19 | 6 | 3 | 90 | 173 | 94955.04 | 182524.688 | 277479.728 | 34820.464 | 267089.0876 | 67.5556 |  |  |  | 7.6705 | #DIV/0! | #DIV/0!
2021-04-20 | 7 | 3 | 160 | 167 | 168808.96 | 176194.352 | 345003.312 | 40835.6789 | 310655.8645 | 71.1111 |  |  |  | 7.6075 | #DIV/0! | #DIV/0!
2021-04-21 | 7 | 3 | 150 | 177 | 158258.4 | 186744.912 | 345003.312 | 43947.5612 | 334581.3399 | 69.3333 |  |  |  | 7.6132 | #DIV/0! | #DIV/0!
2021-04-22 | 7 | 3 | 140 | 174 | 147707.84 | 183579.744 | 331287.584 | 40868.0527 | 314412.215 | 64 |  |  |  | 7.6933 | #DIV/0! | #DIV/0!
2021-04-23 | 7 | 3 | 115 | 174 | 121331.44 | 183579.744 | 304911.184 | 36449.9356 | 283965.0498 | 64 |  |  |  | 7.7906 | #DIV/0! | #DIV/0!
2021-04-24 | 6 | 2 | 65 | 174 | 68578.64 | 183579.744 | 252158.384 | 32805.2874 | 255094.2112 | 60.7917 |  |  |  | 7.776 | #DIV/0! | #DIV/0!
2021-04-25 | 5 | 2 | 60 | 163 | 63303.36 | 171974.128 | 235277.488 | 28997.6793 | 223846.1072 | 60.0278 |  |  |  | 7.7194 | #DIV/0! | #DIV/0!
2021-04-26 | 6 | 2 | 53 | 160 | 55917.968 | 168808.96 | 224726.928 | 27526.0822 | 216578.6012 | 58.7361 |  |  |  | 7.8681 | #DIV/0! | #DIV/0!
2021-04-27 | 7 | 2 | 100 | 174 | 105505.6 | 183579.744 | 289085.344 | 36120.4961 | 281104.9292 | 64 |  |  |  | 7.7824 | #DIV/0! | #DIV/0!
2021-05-19 | 8 | 6 | 200 | 230 | 211011.2 | 242662.88 | 453674.08 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-05-20 | 8 | 7 | 210 | 230 | 221561.76 | 242662.88 | 464224.64 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-05-21 | 8 | 7 | 205 | 230 | 216286.48 | 242662.88 | 458949.36 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-05-22 | 8 | 7 | 213 | 227 | 224726.928 | 239497.712 | 464224.64 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-05-23 | 8 | 7 | 210 | 227 | 221561.76 | 239497.712 | 461059.472 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-05-24 | 8 | 6 | 160 | 227 | 168808.96 | 239497.712 | 408306.672 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-05-25 | 8 | 7 | 205 | 227 | 216286.48 | 239497.712 | 455784.192 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-05-26 | 8 | 6 | 200 | 216 | 211011.2 | 227892.096 | 438903.296 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-06-09 | 8 | 6 | 205 | 206 | 216286.48 | 217341.536 | 433628.016 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-06-10 | 8 | 6 | 210 | 206 | 221561.76 | 217341.536 | 438903.296 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-06-11 | 8 | 6 | 215 | 206 | 226837.04 | 217341.536 | 444178.576 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-06-12 | 8 | 7 | 215 | 199 | 226837.04 | 209956.144 | 436793.184 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-06-13 | 8 | 7 | 190 | 206 | 200460.64 | 217341.536 | 417802.176 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-06-14 | 7 | 6 | 220 | 160 | 232112.32 | 168808.96 | 400921.28 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-06-15 | 8 | 6 | 220 | 206 | 232112.32 | 217341.536 | 449453.856 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-06-16 | 8 | 6 | 220 | 209 | 232112.32 | 220506.704 | 452619.024 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-07-28 | 8 | 7 | 244 | 222 | 257433.664 | 234222.432 | 491656.096 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-07-29 | 8 | 8 | 244 | 222 | 257433.664 | 234222.432 | 491656.096 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-07-30 | 8 | 8 | 244 | 222 | 257433.664 | 234222.432 | 491656.096 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-07-31 | 8 | 7 | 244 | 222 | 257433.664 | 234222.432 | 491656.096 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
2021-08-01 | 8 | 6 | 215 | 220 | 226837.04 | 232112.32 | 458949.36 | 44139.1328 | 353408.0033 | 82.6042 |  |  |  | 8.0067 | #DIV/0! | #DIV/0!
2021-08-02 | 8 | 5 | 185 | 213 | 195185.36 | 224726.928 | 419912.288 | 39052.5 | 319634.9683 | 80 |  |  |  | 8.1848 | #DIV/0! | #DIV/0!
2021-08-03 | 8 | 5 | 215 | 216 | 226837.04 | 227892.096 | 454729.136 | 40480.9199 | 328825.1323 | 85.3333 |  |  |  | 8.123 | #DIV/0! | #DIV/0!
2021-08-04 | 8 | 5 | 200 | 216 | 211011.2 | 227892.096 | 438903.296 | 41225.5918 | 332249.409 | 83.5556 | 329230.7376 | 42304.4105 | 29613087.355 | 8.0593 | 7.7824 | 3.4355
2021-08-18 | 8 | 7 | 244 | 220 | 257433.664 | 232112.32 | 489545.984 | 53632.418 | 412471.0883 | 80.2917 |  |  |  | 7.6907 | #DIV/0! | #DIV/0!
2021-08-19 | 8 | 5 | 240 | 213 | 253213.44 | 224726.928 | 477940.368 | 39527.0957 | 314377.7961 | 81.7778 |  |  |  | 7.9535 | #DIV/0! | #DIV/0!
2021-08-20 | 8 | 5 | 210 | 213 | 221561.76 | 224726.928 | 446288.688 | 46922.375 | 364408.9107 | 83.5556 | 346983.6742 | 45360.5 | 31770350 | 7.7662 | 7.6495 | 1.5032
2021-08-21 | 8 | 6 | 225 | 213 | 237387.6 | 224726.928 | 462114.528 | 47699.0898 | 371918.3179 | 85.3333 |  |  |  | 7.7972 | #DIV/0! | #DIV/0!
2021-08-22 | 8 | 6 | 230 | 213 | 242662.88 | 224726.928 | 467389.808 | 48357.2109 | 381366.6198 | 80 |  |  |  | 7.8864 | #DIV/0! | #DIV/0!
2021-08-23 | 8 | 6 | 210 | 213 | 221561.76 | 224726.928 | 446288.688 | 44636.2773 | 357638.574 | 77.4931 |  |  |  | 8.0123 | #DIV/0! | #DIV/0!
2021-08-24 | 8 | 6 | 230 | 213 | 242662.88 | 224726.928 | 467389.808 | 51517.8828 | 402093.2572 | 80.8472 |  |  |  | 7.8049 | #DIV/0! | #DIV/0!
2021-08-25 | 8 | 7 | 240 | 220 | 253213.44 | 232112.32 | 485325.76 | 52804.3281 | 412789.8566 | 81.6597 |  |  |  | 7.8173 | #DIV/0! | #DIV/0!

## Cost SOD
Generation Costing | [10 empty] | Unit price of PG
15MW
Basic Parameters : |  | Heat Rate Curve (GJ/Hr = AP^2+BP+C) | [8 empty] | Start up | 0
| A | B | C | N Coal ($/T) | N Coal ($/GJ) | Fuel Oil ($/T) | Fuel Oil ($/GJ) | Startup maint cost (HKD) |  |  | 15 MW for 1 hr | 41417
CPA | 0.00037 | 8.3655 | 288.413 |  | 18.894 | 1620.14 | 38.12 | 12000 |  |  | Sum (cost of 15MWh) | 41417
CPB(LCV) | 0.000633 | 7.8036 | 865.308 | LCV ($/T) | LCV ($/GJ) |  |  | 14000 |  |  | Unit cost (HKD) | 2.7611
CPB(gas) | 7.5016e-05 | 8.7482 | 568.03 |  | 14.0825 |  |  | 14000 |  |  | 100MW
CPB(oil) | 0.00014987 | 8.7781 | 496.712 |  |  |  |  | 14000 |  |  | 100 MW for 1 hr | 82707
BKP(ex C5) | 0.002108 | 5.4329 | 443.0661 |  |  |  |  | 70856 |  |  | Sum (cost of 100MWh) | 82707
C5 (upgraded) | 0.00016096 | 6.1436 | 396.9049 | IDO ($/T) | IDO ($/GJ) | GAS ($/GJ) |  |  |  |  | Unit cost (HKD) | 0.82707
BKP(LSIDO) | 0.0032775 | 5.007 | 576.5631 | 4081.43 | 89.72 | 28.1
CPB(normal) | 0.0001671 | 7.9613 | 683.9368 | LSIDO ($/T) | LSIDO ($/GJ) |  |  | 14000 |  |  | 15MW(PG)&85MW(B)
PG1-PG3 | 0.0177 | 7.34 | 321.64 | 1935.48 | 42.67 | [5 empty] | 400MW at B for 1 hr | 172709.1883
[11 empty] | 485MW at B for 1 hr | 202744.3442
Cost Evaluation : | [10 empty] | Diff | 30035.156
| MW | Hour | GJ | SD Hours | Start Up ($) | Running ($) | Total ($) | Incre. ($)/hr | Ave (running) | Ave (TOTAL) | Unit cost of 85MW(B) | 0.35335
CPA | 250 | 12 | 28835 | 8 | 31676.5 | 544808.5 | 576485 | 161.5532 | 181.6028 | 192.1617 | 15MWh(PG)+85MWh(B) | 71452.156
PSPS(LCV) | 300 | 1 | 3121.4 | ---- | ---- | 43957.1 | 43957.1 | 43957.1 | 146.5237 | 146.5237 | Unit cost of this combin | 0.71452
PSPS(gas) | 300 | 1 | 3499.3 | ---- | ---- | 98330.3 | 98330.3 | 98330.3 | 327.7677 | 327.7677
PSPS(BPK) | 300 | 1 | 2173.2 | ---- | ---- | 61066.9 | 61066.9 | 61066.9 | 203.5563 | 203.5563 | Unit cost for A machine
CPB(LCV) | 485 | 3 | 14396.9 | 120 | 102543.7 | 202744.3 | 305288 | 118.541 | 139.3432 | 209.8199 | 250(A) for 1 hr | 45400.3926
BKP(ex C5) | 300 | 1 | 2262.7 | 6 | 76574.4 | 63581.9 | 140156.3 | 188.2054 | 211.9397 | 467.1877 | 350(A) for 1 hr | 61626.5598
C5 (upgraded) | 300 | 1 | 2254.5 | 6 | 76574.4 | 63351.5 | 139925.9 | 175.3502 | 211.1717 | 466.4197 | Diff | 16226.1672
CPB(GAS) | 600 | 1 | 5844 | 6 | 49152 | 164216.4 | 213368.4 | 248.354 | 273.694 | 355.614 | Unit cost (A) | 0.16226
CPB(normal) | 600 | 1 | 5520.9 | 6 | 49152 | 104311.8846 | 153463.9 | 311.1286 | 173.8531 | 255.7732
CPB(Oil) | 615 | 1 | 5951.9 | 6 | 49152 | 226886.428 | 276038.4 | 341.6482 | 368.921 | 448.8429 | Cost of 75MW PG | 66947.9
PG1-PG3 | 15 | 1 | 435.7 | ---- | 2326.4151 | 39091.004 | 41417.4 | 706.1861 | 2606.0669 | 2761.16 | Unit cost 75MW PG | 0.89264
BKP(LSIDO) | 240 | 9 | 17703.3 | 8 | 79730 | 755399.8 | 835129.8 | 280.7786 | 349.7221 | 386.6342
Minimum Down Time : | [10 empty] | Cost of 25MW B | 14938.716
| MW | Hour | GJ | SD Hours | Start Up ($) | No Load ($) | No Load-Start Up ($) |  | 136050.7 | 41417.4 | Cost at 400 MW | 172709.1883
CPA | 0 | 1 | 288.4 | 25.6 | 40170.7 | 5449 | -34721.7 |  | 115895.7 | 20155 | Cost at 425 MW | 181502.3012
CPB(LCV) | 0 | 5 | 4326.5 | 5 | 14000 | 60927.9 | 46927.9 |  |  | 61572.4 | Diff (cost of 25MW) | 8793.113
[8 empty] | COST | 42000 |  | Unit cost | 0.35172
|  | Generation Cost/hour | [7 empty] | 19572.4 | Corresponding PS cost | 0.46897
Unit | Min. Load | $ at min. | $ no load | Target load | $ at Target | $ at F.L. | $ marg. | $ avg/MW
A | 300 | 53495.7752 | 5449.2751 | 250 | 45400.6405 | 58369.634 | 161.5601 | 181.6026 |  |  | From PSPS(LCV)
B | 220 | 36793.8716 | 16349.1294 | 400 | 57569.6543 | 122139.4165 | 117.0345 | 143.9241
C | 300 | 63351.0054 | 12450.1574 | 300 | 63351.0054 | 66859.8181 | 175.3547 | 211.17 |  |  | Unit cost of this combination of 75MW(PG)+25MW(PS)
PG | 15 | 8232.5413 | 12922.3019 | 15 | 39093.0243 | 23289.5008 | 707.7742 | 2606.2016 |  |  | 0.78672
PS* | 180 | 38141.4538 | -9905.0463 | 300 | 63569.0897 | 63569.0897 | 211.897 | 211.897
Note : *PS assuming pumping by CPB units at marginal rate
1 kcal = 4186.8 J = 426.9 kp.m = 1.163 10-3 kWh = 3.088 ft.lbf = 3.9683 Btu = 1000 cal

## BKP ST UP
Black Point Start Up Heat Rate Curve
SD Hours | Gas (GJ) | Aux. Energy | Total Gas (GJ)
0 | 0 | 0 | 0
1
2
3
4
5
6 | 119.8 | 83.7 | 203.5
7 | 178.3 | 85.4 | 263.7
8 | 228.7 | 87.1 | 315.8
9 | 271.5 | 88.8 | 360.3
10 | 307.6 | 90.5 | 398.1
11 | 338.1 | 92.1 | 430.2
12 | 363.7 | 93.7 | 457.4
13 | 385.4 | 95.3 | 480.7
14 | 403.8 | 96.9 | 500.7
15 | 419.4 | 98.4 | 517.8
16 | 432.8 | 100 | 532.8
17 | 444.2 | 101.5 | 545.7
18 | 454 | 102.9 | 556.9
19 | 462.4 | 104.4 | 566.8
20 | 469.7 | 105.9 | 575.6
21 | 476 | 107.3 | 583.3
22 | 481.5 | 108.7 | 590.2
23 | 486.3 | 110.1 | 596.4
24 | 490.4 | 111.4 | 601.8
25 | 494 | 112.7 | 606.7
26 | 497.2 | 114.1 | 611.3
27 | 499.9 | 115.4 | 615.3
28 | 502.3 | 116.6 | 618.9
29 | 504.4 | 117.9 | 622.3
30 | 506.2 | 119.1 | 625.3
31 | 507.8 | 120.3 | 628.1
32 | 509.2 | 121.5 | 630.7
33 | 510.4 | 122.7 | 633.1
34 | 511.4 | 123.8 | 635.2
35 | 512.3 | 124.9 | 637.2
36 | 513 | 126 | 639
37 | 513.7 | 127.1 | 640.8
38 | 514.2 | 128.2 | 642.4
39 | 514.7 | 129.2 | 643.9
40 | 515 | 130.2 | 645.2
41 | 515.3 | 131.29 | 646.59
42 | 515.6 | 132.34 | 647.94
43 | 515.9 | 133.39 | 649.29
44 | 516.2 | 134.44 | 650.64
45 | 516 | 135 | 651
46 | 516 | 135.8867 | 651.8867
47 | 516 | 136.6917 | 652.6917
48 | 516 | 137.4967 | 653.4967
49 | 516 | 138.3017 | 654.3017
50 | 515.9 | 139.2 | 655.1
51 | 515.8 | 140.0361 | 655.8361
52 | 515.7 | 140.8878 | 656.5878
53 | 515.6 | 141.7394 | 657.3394
54 | 515.5 | 142.5911 | 658.0911
55 | 515.4 | 142.9 | 658.3
56 | 515.25 | 143.7517 | 659.0017
57 | 515.1 | 144.4405 | 659.5405
58 | 514.95 | 145.1293 | 660.0793
59 | 514.8 | 145.8182 | 660.6182
60 | 514.7 | 146 | 660.7
61 | 514.6 | 146.6888 | 661.2888
62 | 514.5 | 147.2256 | 661.7256
63 | 514.4 | 147.7623 | 662.1623
64 | 514.3 | 148.299 | 662.599
65 | 514.1 | 148.6 | 662.7
66 | 513.95 | 149.1367 | 663.0867
67 | 513.8 | 149.6027 | 663.4027
68 | 513.65 | 150.0687 | 663.7187
69 | 513.5 | 150.5347 | 664.0347
70 | 513.5 | 150.7 | 664.2
71 | 513.5 | 151.0658 | 664.5658
72 | 513.5 | 151.3814 | 664.8814
73 | 513.5 | 151.697 | 665.197
74 | 513.5 | 152.0126 | 665.5126
75 | 513.3 | 152.2 | 665.5
76 | 513.3 | 152.3874 | 665.6874
77 | 513.3 | 152.5747 | 665.8747
78 | 513.3 | 152.7621 | 666.0621
79 | 513.3 | 152.9494 | 666.2494
80 | 513.3 | 153.2 | 666.5

## df_gen
Unit | committable | p_min_pu | p_max_pu | marginal_cost | min_down_time | min_up_time | up_time_before | down_time_before | ramp_limit_up | ramp_limit_down | ramp_limit_start_up | ramp_limit_shut_down | shut_down_cost | start_up_cost | efficiency | p_nom | p_nom_min | p_nom_max
C1 | FALSE | 0.55 | 1 | 175 | 24 | 48 | 96 | 0 | 0.4 | 0.5 | 0.5 | 0.5 | 15000 | 18000 | 46.8565 | 345 | 300 | 345
C2 | FALSE | 0.53 | 1 | 175 | 24 | 48 | 96 | 0 | 0.4 | 0.5 | 0.5 | 0.5 | 15000 | 18000 | 48.0994 | 355 | 260 | 355
C3 | FALSE | 0.75 | 1 | 175 | 24 | 48 | 0 | 10 | 0.4 | 0.5 | 0.5 | 0.5 | 15000 | 18000 | 45.8865 | 330 | 50 | 330
C4 | TRUE | 0 | 1 | 175 | 24 | 48 | 0 | 7 | 0.4 | 0.5 | 0.5 | 0.5 | 15000 | 18000 | 44.3082 | 315 | 50 | 315
C5 | FALSE | 0.52 | 1 | 175 | 24 | 48 | 96 | 0 | 0.4 | 0.5 | 0.5 | 0.5 | 15000 | 18000 | 48.7032 | 355 | 180 | 355
C6 | TRUE | 0 | 1 | 175 | 24 | 48 | 70 | 0 | 0.4 | 0.5 | 0.5 | 0.5 | 15000 | 18000 | 46.0923 | 350 | 50 | 350
C7 | FALSE | 0.76 | 1 | 175 | 24 | 48 | 0 | 96 | 0.4 | 0.5 | 0.5 | 0.5 | 15000 | 9000 | 0 | 0 | 0 | 0
C8 | TRUE | 0 | 1 | 175 | 24 | 48 | 0 | 3 | 0.4 | 0.5 | 0.5 | 0.5 | 15000 | 18000 | 46.5329 | 350 | 50 | 350

## load
TIME | 0:00 | 0:15 | 0:30 | 0:45 | 1:00 | 1:15 | 1:30 | 1:45 | 2:00 | 2:15 | 2:30 | 2:45 | 3:00 | 3:15 | 3:30 | 3:45 | 4:00 | 4:15 | 4:30 | 4:45 | 5:00 | 5:15 | 5:30 | 5:45 | 6:00 | 6:15 | 6:30 | 6:45 | 7:00 | 7:15 | 7:30 | 7:45 | 8:00 | 8:15 | 8:30 | 8:45 | 9:00 | 9:15 | 9:30 | 9:45 | 10:00 | 10:15 | 10:30 | 10:45 | 11:00 | 11:15 | 11:30 | 11:45 | 12:00 | 12:15 | 12:30 | 12:45 | 13:00 | 13:15 | 13:30 | 13:45 | 14:00 | 14:15 | 14:30 | 14:45 | 15:00 | 15:15 | 15:30 | 15:45 | 16:00 | 16:15 | 16:30 | 16:45 | 17:00 | 17:15 | 17:30 | 17:45 | 18:00 | 18:15 | 18:30 | 18:45 | 19:00 | 19:15 | 19:30 | 19:45 | 20:00 | 20:15 | 20:30 | 20:45 | 21:00 | 21:15 | 21:30 | 21:45 | 22:00 | 22:15 | 22:30 | 22:45 | 23:00 | 23:15 | 23:30 | 23:45
C1 | 323.7093 | 324.1081 | 324.507 | 324.9058 | 325.3047 | 325.7036 | 326.1024 | 326.5013 | 326.9001 | 327.299 | 327.6979 | 328.0967 | 328.4956 | 328.8944 | 329.2933 | 329.6922 | 330.091 | 330.4899 | 330.8888 | 331.2876 | 331.6865 | 332.0853 | 332.4842 | 332.8831 | 333.2819 | 333.6808 | 334.0797 | 334.4785 | 334.8774 | 335.2762 | 335.6751 | 336.0739 | 336.4728 | 336.8717 | 337.2705 | 337.6694 | 338.0683 | 338.4671 | 338.866 | 339.2649 | 339.6637 | 340.0626 | 340.4614 | 343.3459 | 342.2887 | 342.9202 | 343.5517 | 344.1832 | 334.1896 | 343.9611 | 338.9504 | 342.7713 | 336.0608 | 327.5696 | 329.3287 | 343.2034 | 343.7231 | 342.4189 | 344.0266 | 344.5864 | 343.3501 | 343.5976 | 342.62 | 343.44 | 343.3132 | 342.6627 | 343.1526 | 343.689 | 338.7837 | 343.5609 | 343.0087 | 343.7733 | 340.1787 | 341.612 | 342.6743 | 305.0746 | 299.3424 | 301.4093 | 297.1726 | 296.4291 | 290.8466 | 252.1573 | 255.437 | 299.0841 | 298.0211 | 342.6691 | 313.9113 | 317.561 | 343.7697 | 344.1253 | 340.4113 | 343.4877 | 340.6537 | 339.9626 | 340.7925 | 338.7815
C2 | 323.9623 | 323.2374 | 322.5125 | 321.7876 | 321.0627 | 320.3378 | 319.6129 | 318.888 | 318.1631 | 317.4382 | 316.7133 | 315.9884 | 315.2635 | 314.5386 | 313.8137 | 313.0888 | 312.3639 | 311.639 | 310.9141 | 310.1892 | 309.4643 | 308.7394 | 308.0145 | 307.2896 | 306.5647 | 305.8398 | 305.1149 | 304.39 | 303.6651 | 302.9402 | 302.2153 | 301.4904 | 300.7655 | 300.0406 | 299.3157 | 298.5908 | 297.8659 | 297.141 | 296.4161 | 295.6912 | 294.9663 | 294.2414 | 293.5165 | 296.974 | 292.3531 | 294.6197 | 296.8864 | 299.153 | 281.6751 | 295.9052 | 285.5453 | 288.7293 | 279.5137 | 272.8499 | 279.7388 | 348.7494 | 348.3325 | 348.2379 | 346.0045 | 346.903 | 328.8164 | 327.7542 | 308.6276 | 301.926 | 296.2047 | 296.1075 | 293.8745 | 295.7542 | 288.0163 | 293.9495 | 308.9925 | 319.9541 | 310.9742 | 323.0392 | 304.4686 | 276.6285 | 262.2875 | 282.42 | 283.6802 | 253.4211 | 240.7453 | 199.6553 | 203.2813 | 265.0213 | 241.7566 | 276.201 | 258.5173 | 262.5756 | 346.2041 | 335.5615 | 283.4466 | 321.6507 | 325.6957 | 332.614 | 292.1002 | 283.4847
C3 | 303.0018 | 303.6074 | 304.213 | 304.8186 | 305.4241 | 306.0297 | 306.6353 | 307.2408 | 307.8464 | 308.452 | 309.0576 | 309.6631 | 310.2687 | 310.8743 | 311.4799 | 312.0854 | 312.691 | 313.2966 | 313.9022 | 314.5078 | 315.1133 | 315.7189 | 316.3245 | 316.93 | 317.5356 | 318.1412 | 318.7468 | 319.3523 | 319.9579 | 320.5635 | 321.1691 | 321.7746 | 322.3802 | 322.9858 | 323.5913 | 324.1969 | 324.8025 | 325.4081 | 326.0136 | 326.6192 | 327.2248 | 327.8304 | 328.4359 | 329.2034 | 328.8388 | 328.4052 | 327.9715 | 327.5378 | 328.9677 | 326.4425 | 328.0395 | 328.3003 | 328.8842 | 328.744 | 329.1574 | 328.8077 | 329.0805 | 329.6416 | 329.591 | 329.9492 | 329.3389 | 328.2266 | 330.2898 | 330.2174 | 331.0996 | 329.7017 | 330.2104 | 328.5901 | 330.3434 | 330.0676 | 331.0119 | 331.5405 | 333.4861 | 333.7952 | 333.9871 | 333.8542 | 333.1182 | 330.644 | 331.9168 | 333.7901 | 333.3796 | 335.837 | 306.2208 | 40.9771 | 22.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C4 | 309.6364 | 309.667 | 309.6976 | 309.7283 | 309.7589 | 309.7895 | 309.8202 | 309.8508 | 309.8814 | 309.912 | 309.9427 | 309.9733 | 310.0039 | 310.0346 | 310.0652 | 310.0958 | 310.1265 | 310.1571 | 310.1877 | 310.2184 | 310.249 | 310.2796 | 310.3102 | 310.3409 | 310.3715 | 310.4021 | 310.4328 | 310.4634 | 310.494 | 310.5247 | 310.5553 | 310.5859 | 310.6165 | 310.6472 | 310.6778 | 310.7084 | 310.7391 | 310.7697 | 310.8003 | 310.831 | 310.8616 | 310.8922 | 310.9229 | 311.1515 | 311.5096 | 310.9732 | 310.4368 | 309.9004 | 310.1674 | 310.0803 | 311.8275 | 311.43 | 311.7146 | 311.9582 | 312.4726 | 287.5713 | 270.9825 | 263.1235 | 269.1251 | 266.7021 | 258.8406 | 260.2316 | 265.9059 | 262.4769 | 261.7037 | 264.075 | 264.3502 | 264.2917 | 263.4932 | 265.0359 | 265.1454 | 267.5056 | 260.7094 | 264.6632 | 268.0764 | 265.2972 | 261.6033 | 265.4576 | 262.527 | 261.6601 | 259.052 | 263.3625 | 260.1573 | 260.6788 | 259.2613 | 33.2577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C5 | 341.8268 | 340.7777 | 339.7287 | 338.6796 | 337.6305 | 336.5815 | 335.5324 | 334.4833 | 333.4342 | 332.3851 | 331.3361 | 330.287 | 329.2379 | 328.1888 | 327.1398 | 326.0907 | 325.0416 | 323.9926 | 322.9435 | 321.8944 | 320.8453 | 319.7962 | 318.7472 | 317.6981 | 316.649 | 315.5999 | 314.5509 | 313.5018 | 312.4527 | 311.4037 | 310.3546 | 309.3055 | 308.2564 | 307.2074 | 306.1583 | 305.1092 | 304.0601 | 303.011 | 301.962 | 300.9129 | 299.8638 | 298.8148 | 297.7657 | 300.6579 | 302.4879 | 301.6051 | 300.7223 | 299.8395 | 287.2591 | 305.832 | 293.6468 | 296.3462 | 289.0194 | 278.9621 | 275.5902 | 355.2068 | 356.4487 | 352.2515 | 340.9683 | 354.481 | 345.7298 | 336.2251 | 320.4031 | 306.956 | 310.4467 | 296.2591 | 293.0213 | 298.493 | 295.5878 | 300.3871 | 309.536 | 318.8388 | 325.3785 | 326.2612 | 309.6123 | 289.0823 | 269.8623 | 284.3461 | 298.1721 | 264.7243 | 260.3535 | 260.0917 | 260.2492 | 268.4442 | 259.938 | 286.5318 | 266.8761 | 269.6903 | 344.5015 | 341.4692 | 290.1877 | 327.0896 | 343.004 | 339.5175 | 298.9724 | 290.6682
C6 | 322.6375 | 323.0761 | 323.5147 | 323.9533 | 324.3919 | 324.8305 | 325.2691 | 325.7077 | 326.1463 | 326.5849 | 327.0234 | 327.462 | 327.9006 | 328.3392 | 328.7778 | 329.2164 | 329.655 | 330.0936 | 330.5322 | 330.9708 | 331.4094 | 331.8479 | 332.2865 | 332.7251 | 333.1637 | 333.6023 | 334.0409 | 334.4795 | 334.9181 | 335.3567 | 335.7953 | 336.2339 | 336.6724 | 337.111 | 337.5496 | 337.9882 | 338.4268 | 338.8654 | 339.304 | 339.7426 | 340.1812 | 340.6198 | 341.0583 | 340.3197 | 342.2361 | 342.738 | 343.24 | 343.7419 | 330.3667 | 344.7427 | 336.9229 | 339.0511 | 329.3561 | 323.427 | 325.2557 | 344.2319 | 345.8948 | 344.2079 | 344.7951 | 345.4404 | 343.1141 | 346.18 | 344.3925 | 344.3839 | 342.2727 | 342.5065 | 341.6599 | 342.6392 | 339.1524 | 344.2888 | 344.65 | 344.2069 | 339.5901 | 344.2862 | 343.4885 | 335.8175 | 311.2177 | 329.2299 | 343.7488 | 306.5214 | 284.3823 | 248.6552 | 249.2058 | 312.2392 | 296.8223 | 344.515 | 316.968 | 311.2158 | 345.292 | 344.7178 | 334.8863 | 213.7505 | 98.067 | 19.8901 | 0 | 0
C7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C8 | 325.24 | 325.875 | 326.51 | 327.1451 | 327.7801 | 328.4151 | 329.0501 | 329.6851 | 330.3202 | 330.9552 | 331.5902 | 332.2252 | 332.8602 | 333.4952 | 334.1302 | 334.7653 | 335.4003 | 336.0353 | 336.6703 | 337.3053 | 337.9403 | 338.5753 | 339.2104 | 339.8454 | 340.4804 | 341.1154 | 341.7505 | 342.3855 | 343.0205 | 343.6555 | 344.2905 | 344.9255 | 345.5605 | 346.1956 | 346.8306 | 347.4656 | 348.1006 | 348.7356 | 349.3706 | 350.0057 | 350.6407 | 351.2757 | 351.9107 | 353.8381 | 354.3801 | 353.7717 | 353.1633 | 352.5549 | 353.5723 | 353.6505 | 353.6954 | 352.6909 | 353.2646 | 354.0097 | 353.5493 | 354.1846 | 354.4188 | 355.1234 | 354.0693 | 353.8391 | 354.5042 | 353.1191 | 355.874 | 356.0341 | 355.9181 | 354.8976 | 355.7705 | 355.3003 | 356.2727 | 356.0973 | 356.025 | 356.2363 | 356.7964 | 357.2805 | 356.8765 | 357.7213 | 359.745 | 360.9062 | 361.5924 | 361.2387 | 361.6572 | 362.3405 | 362.6646 | 364.5739 | 364.8547 | 364.7828 | 365.6444 | 364.5836 | 39.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total load | 2250.0141 | 2250.3488 | 2250.6835 | 2251.0182 | 2251.3529 | 2251.6877 | 2252.0223 | 2252.357 | 2252.6917 | 2253.0264 | 2253.3611 | 2253.6958 | 2254.0305 | 2254.3652 | 2254.6999 | 2255.0346 | 2255.3693 | 2255.704 | 2256.0387 | 2256.3734 | 2256.7081 | 2257.0428 | 2257.3775 | 2257.7122 | 2258.0469 | 2258.3815 | 2258.7163 | 2259.051 | 2259.3857 | 2259.7204 | 2260.0551 | 2260.3898 | 2260.7245 | 2261.0592 | 2261.3938 | 2261.7286 | 2262.0633 | 2262.398 | 2262.7327 | 2263.0674 | 2263.4021 | 2263.7367 | 2264.0715 | 2275.4904 | 2274.0943 | 2275.0331 | 2275.9719 | 2276.9107 | 2226.198 | 2280.6142 | 2248.6279 | 2259.3192 | 2227.8134 | 2197.5204 | 2205.0927 | 2361.9551 | 2348.881 | 2335.0047 | 2328.5799 | 2341.9014 | 2303.6942 | 2295.3342 | 2268.113 | 2245.4343 | 2240.9588 | 2226.2101 | 2222.0392 | 2228.7574 | 2211.6494 | 2233.3871 | 2258.3694 | 2282.0555 | 2267.1135 | 2290.9375 | 2259.1837 | 2163.4756 | 2097.1764 | 2154.413 | 2178.8099 | 2077.7848 | 2030.4165 | 1922.0993 | 1897.2159 | 1811.0187 | 1742.6559 | 1647.9575 | 1521.9172 | 1525.6262 | 1419.6587 | 1365.8738 | 1248.9318 | 1205.9785 | 1107.4204 | 1031.9843 | 931.8651 | 912.9345

## df_load
| 0 | 1 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96
Load | 2250 | 2250 | 2251 | 2251 | 2251 | 2252 | 2252 | 2252 | 2253 | 2253 | 2253 | 2254 | 2254 | 2254 | 2255 | 2255 | 2255 | 2256 | 2256 | 2256 | 2257 | 2257 | 2257 | 2258 | 2258 | 2258 | 2259 | 2259 | 2259 | 2260 | 2260 | 2260 | 2261 | 2261 | 2261 | 2262 | 2262 | 2262 | 2263 | 2263 | 2263 | 2264 | 2264 | 2275 | 2274 | 2275 | 2276 | 2277 | 2226 | 2281 | 2249 | 2259 | 2228 | 2198 | 2205 | 2362 | 2349 | 2335 | 2329 | 2342 | 2304 | 2295 | 2268 | 2245 | 2241 | 2226 | 2222 | 2229 | 2212 | 2233 | 2258 | 2282 | 2267 | 2291 | 2259 | 2163 | 2097 | 2154 | 2179 | 2078 | 2030 | 1922 | 1897 | 1811 | 1743 | 1648 | 1522 | 1526 | 1420 | 1366 | 1249 | 1206 | 1107 | 1032 | 932 | 913

## df_gen_200820
Unit | committable | p_min_pu | p_max_pu | marginal_cost | min_down_time | min_up_time | up_time_before | down_time_before | ramp_limit_up | ramp_limit_down | ramp_limit_start_up | ramp_limit_shut_down | shut_down_cost | start_up_cost | efficiency | p_nom | p_nom_min | p_nom_max
C1 | FALSE | 0.55 | 1 | 175 | 16 | 72 | 96 | 0 | 0.25 | 0.25 | 0 | 0.5 | 15000 | 18000 | 45.9515 | 330 | 180 | 330
C2 | FALSE | 0.53 | 1 | 175 | 16 | 72 | 96 | 0 | 0.25 | 0.25 | 0 | 0.5 | 15000 | 18000 | 46.1393 | 340 | 180 | 340
C3 | FALSE | 0.75 | 1 | 175 | 16 | 72 | 96 | 0 | 0.25 | 0.25 | 0 | 0.5 | 15000 | 18000 | 48.0267 | 320 | 260 | 320
C4 | TRUE | 0 | 1 | 175 | 16 | 72 | 0 | 1 | 0.25 | 0.25 | 0.25 | 0.5 | 15000 | 18000 | 44.3495 | 305 | 50 | 305
C5 | FALSE | 0.52 | 1 | 175 | 16 | 72 | 96 | 0 | 0.25 | 0.25 | 0 | 0.5 | 15000 | 18000 | 46.9292 | 345 | 180 | 345
C6 | TRUE | 0 | 1 | 175 | 16 | 72 | 67 | 0 | 0.25 | 0.25 | 0.25 | 0.5 | 15000 | 18000 | 45.1683 | 335 | 50 | 335
C7 | FALSE | 0.76 | 1 | 175 | 16 | 72 | 96 | 0 | 0.25 | 0.25 | 0 | 0.5 | 15000 | 18000 | 46.9411 | 315 | 260 | 315
C8 | TRUE | 0 | 1 | 175 | 16 | 72 | 70 | 0 | 0.25 | 0.25 | 0.25 | 0.5 | 15000 | 18000 | 46.1532 | 340 | 50 | 340

## load_200820
TIME | 0:00 | 0:15 | 0:30 | 0:45 | 1:00 | 1:15 | 1:30 | 1:45 | 2:00 | 2:15 | 2:30 | 2:45 | 3:00 | 3:15 | 3:30 | 3:45 | 4:00 | 4:15 | 4:30 | 4:45 | 5:00 | 5:15 | 5:30 | 5:45 | 6:00 | 6:15 | 6:30 | 6:45 | 7:00 | 7:15 | 7:30 | 7:45 | 8:00 | 8:15 | 8:30 | 8:45 | 9:00 | 9:15 | 9:30 | 9:45 | 10:00 | 10:15 | 10:30 | 10:45 | 11:00 | 11:15 | 11:30 | 11:45 | 12:00 | 12:15 | 12:30 | 12:45 | 13:00 | 13:15 | 13:30 | 13:45 | 14:00 | 14:15 | 14:30 | 14:45 | 15:00 | 15:15 | 15:30 | 15:45 | 16:00 | 16:15 | 16:30 | 16:45 | 17:00 | 17:15 | 17:30 | 17:45 | 18:00 | 18:15 | 18:30 | 18:45 | 19:00 | 19:15 | 19:30 | 19:45 | 20:00 | 20:15 | 20:30 | 20:45 | 21:00 | 21:15 | 21:30 | 21:45 | 22:00 | 22:15 | 22:30 | 22:45 | 23:00 | 23:15 | 23:30 | 23:45
C1 | 223 | 180 | 278 | 192 | 266 | 200 | 306 | 236 | 180 | 180 | 180 | 180 | 180 | 323 | 298 | 282 | 265 | 255 | 240 | 244 | 271 | 286 | 321 | 180 | 180 | 180 | 182 | 184 | 180 | 180 | 216 | 199 | 196 | 190 | 180 | 199 | 253 | 253 | 253 | 271 | 308 | 271 | 290 | 298 | 304 | 308 | 326 | 329 | 330 | 326 | 326 | 326 | 326 | 308 | 308 | 308 | 295 | 290 | 290 | 290 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 303 | 290 | 313 | 290 | 253 | 235 | 220 | 199 | 271 | 235 | 209 | 245 | 199 | 180 | 180 | 217
C2 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 186 | 186 | 180 | 204 | 247 | 260 | 260 | 279 | 297 | 279 | 279 | 297 | 297 | 316 | 316 | 334 | 340 | 334 | 333 | 316 | 319 | 316 | 305 | 297 | 297 | 294 | 279 | 281 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 297 | 279 | 316 | 280 | 260 | 241 | 223 | 186 | 260 | 240 | 204 | 241 | 204 | 180 | 180 | 205
C3 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 100 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 298 | 287 | 284 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 286 | 283 | 305 | 305 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 0
C5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 199 | 199 | 180 | 199 | 253 | 253 | 253 | 271 | 308 | 282 | 290 | 290 | 308 | 321 | 326 | 344 | 345 | 326 | 326 | 326 | 326 | 326 | 308 | 308 | 308 | 290 | 290 | 290 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 308 | 290 | 326 | 290 | 253 | 235 | 217 | 186 | 268 | 235 | 217 | 235 | 199 | 180 | 180 | 217
C6 | 227 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 100 | 193 | 192 | 192 | 180 | 208 | 244 | 250 | 250 | 273 | 300 | 279 | 287 | 296 | 296 | 314 | 325 | 331 | 335 | 331 | 331 | 324 | 331 | 314 | 314 | 302 | 296 | 296 | 284 | 296 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 296 | 284 | 314 | 296 | 254 | 233 | 227 | 192 | 261 | 227 | 209 | 244 | 198 | 180 | 180 | 209
C7 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 291 | 291 | 291 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 291 | 285 | 315 | 315 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
C8 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 100 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 190 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 225 | 340 | 340 | 340 | 264 | 234 | 224 | 217 | 237 | 212 | 226 | 242 | 246 | 246 | 264 | 180 | 340 | 340 | 340 | 340 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
Total load | 1510 | 1420 | 1338 | 1252 | 1326 | 1260 | 1186 | 1116 | 1060 | 1060 | 1060 | 1060 | 1060 | 1203 | 1178 | 1162 | 1145 | 1135 | 1120 | 1124 | 1151 | 1166 | 1201 | 1060 | 1060 | 1060 | 1112 | 1164 | 1240 | 1290 | 1376 | 1452 | 1603 | 1647 | 1780 | 1870 | 2057 | 2076 | 2076 | 2154 | 2273 | 2171 | 2206 | 2241 | 2265 | 2319 | 2353 | 2398 | 2420 | 2377 | 2376 | 2352 | 2362 | 2324 | 2295 | 2275 | 2256 | 2230 | 2203 | 2217 | 2455 | 2599 | 2588 | 2585 | 2494 | 2464 | 2454 | 2447 | 2467 | 2442 | 2456 | 2472 | 2476 | 2476 | 2494 | 2410 | 2587 | 2578 | 2630 | 2630 | 2264 | 2203 | 2329 | 2216 | 2080 | 2004 | 1947 | 1823 | 2120 | 1997 | 1899 | 2025 | 1860 | 1780 | 1780 | 1628

## df_load_200820
| 0 | 1 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96
Load | 1510 | 1420 | 1338 | 1252 | 1326 | 1260 | 1186 | 1116 | 1060 | 1060 | 1060 | 1060 | 1060 | 1203 | 1178 | 1162 | 1145 | 1135 | 1120 | 1124 | 1151 | 1166 | 1201 | 1060 | 1060 | 1060 | 1112 | 1164 | 1240 | 1290 | 1376 | 1452 | 1603 | 1647 | 1780 | 1870 | 2057 | 2076 | 2076 | 2154 | 2273 | 2171 | 2206 | 2241 | 2265 | 2319 | 2353 | 2398 | 2420 | 2377 | 2376 | 2352 | 2362 | 2324 | 2295 | 2275 | 2256 | 2230 | 2203 | 2217 | 2455 | 2599 | 2588 | 2585 | 2494 | 2464 | 2454 | 2447 | 2467 | 2442 | 2456 | 2472 | 2476 | 2476 | 2494 | 2410 | 2587 | 2578 | 2630 | 2630 | 2264 | 2203 | 2329 | 2216 | 2080 | 2004 | 1947 | 1823 | 2120 | 1997 | 1899 | 2025 | 1860 | 1780 | 1780 | 1628

## df_gen_200804
Unit | committable | p_min_pu | p_max_pu | marginal_cost | min_down_time | min_up_time | up_time_before | down_time_before | ramp_limit_up | ramp_limit_down | ramp_limit_start_up | ramp_limit_shut_down | shut_down_cost | start_up_cost | efficiency | p_nom | p_nom_min | p_nom_max
C1 | FALSE | 0.55 | 1 | 175 | 24 | 48 | 96 | 0 | 0.4 | 0.5 | 0 | 0.5 | 13000 | 18000 | 42.8497 | 326 | 180 | 326
C2 | FALSE | 0.53 | 1 | 175 | 24 | 48 | 96 | 0 | 0.4 | 0.5 | 0 | 0.5 | 13000 | 18000 | 42.9922 | 334 | 180 | 334
C3 | TRUE | 0.75 | 1 | 175 | 24 | 48 | 70 | 0 | 0.4 | 0.5 | 0.1 | 0.5 | 13000 | 18000 | 45.5418 | 320 | 50 | 320
C4 | FALSE | 0 | 1 | 175 | 24 | 48 | 96 | 0 | 0.4 | 0.5 | 0 | 0.5 | 13000 | 18000 | 44.9298 | 260 | 260 | 260
C5 | FALSE | 0.52 | 1 | 175 | 24 | 48 | 96 | 0 | 0.4 | 0.5 | 0 | 0.5 | 13000 | 18000 | 43.6448 | 180 | 180 | 180
C6 | TRUE | 0 | 1 | 175 | 24 | 48 | 64 | 0 | 0.4 | 0.5 | 0.1 | 0.5 | 13000 | 18000 | 45.369 | 331 | 50 | 331
C7 | TRUE | 0.76 | 1 | 175 | 24 | 48 | 67 | 0 | 0.4 | 0.5 | 0.1 | 0.5 | 13000 | 18000 | 44.9894 | 260 | 50 | 260
C8 | FALSE | 0 | 1 | 175 | 24 | 48 | 96 | 0 | 0.4 | 0.5 | 0 | 0.5 | 13000 | 18000 | 46.5297 | 327 | 180 | 327

## load_200804
TIME | 0:00 | 0:15 | 0:30 | 0:45 | 1:00 | 1:15 | 1:30 | 1:45 | 2:00 | 2:15 | 2:30 | 2:45 | 3:00 | 3:15 | 3:30 | 3:45 | 4:00 | 4:15 | 4:30 | 4:45 | 5:00 | 5:15 | 5:30 | 5:45 | 6:00 | 6:15 | 6:30 | 6:45 | 7:00 | 7:15 | 7:30 | 7:45 | 8:00 | 8:15 | 8:30 | 8:45 | 9:00 | 9:15 | 9:30 | 9:45 | 10:00 | 10:15 | 10:30 | 10:45 | 11:00 | 11:15 | 11:30 | 11:45 | 12:00 | 12:15 | 12:30 | 12:45 | 13:00 | 13:15 | 13:30 | 13:45 | 14:00 | 14:15 | 14:30 | 14:45 | 15:00 | 15:15 | 15:30 | 15:45 | 16:00 | 16:15 | 16:30 | 16:45 | 17:00 | 17:15 | 17:30 | 17:45 | 18:00 | 18:15 | 18:30 | 18:45 | 19:00 | 19:15 | 19:30 | 19:45 | 20:00 | 20:15 | 20:30 | 20:45 | 21:00 | 21:15 | 21:30 | 21:45 | 22:00 | 22:15 | 22:30 | 22:45 | 23:00 | 23:15 | 23:30 | 23:45
C1 | 180.0088 | 187.2827 | 181.6317 | 179.9696 | 180.1108 | 179.8873 | 179.8932 | 180.0407 | 179.9988 | 179.8538 | 179.8645 | 179.8413 | 180.069 | 179.7669 | 179.9436 | 179.8062 | 179.9304 | 179.5882 | 179.8456 | 179.3052 | 179.1269 | 179.7463 | 179.9237 | 179.769 | 179.8592 | 179.9734 | 180.0734 | 180.0784 | 180.2409 | 180.0299 | 180.107 | 180.0235 | 180.0794 | 180.127 | 181.9032 | 198.9898 | 231.6952 | 193.5744 | 195.3176 | 223.6196 | 239.6519 | 252.1251 | 206.7724 | 204.8416 | 227.434 | 246.3714 | 252.1972 | 255.978 | 256.606 | 258.5053 | 258.6052 | 258.69 | 258.882 | 258.7899 | 253.3124 | 238.8098 | 228.6297 | 218.8736 | 206.8649 | 220.5251 | 216.1412 | 190.6501 | 182.3734 | 180.1541 | 180.0885 | 179.9611 | 180.0578 | 180.0001 | 180.0576 | 186.6808 | 199.3782 | 201.9146 | 196.4649 | 209.3674 | 235.2636 | 242.6687 | 260.057 | 265.4461 | 266.3286 | 261.3019 | 249.4307 | 266.3865 | 225.4487 | 190.4037 | 180.8951 | 182.9656 | 189.2062 | 180.787 | 180.6286 | 180.3508 | 179.8331 | 180.1022 | 180.5009 | 180.4392 | 179.9818 | 185.6117
C2 | 179.9869 | 185.2073 | 180.6073 | 180.0649 | 180.0477 | 179.9804 | 179.9219 | 180.0623 | 179.8999 | 179.8865 | 179.9027 | 179.8538 | 179.9724 | 179.9337 | 179.8534 | 179.7822 | 180.0272 | 179.6587 | 179.8377 | 179.1342 | 179.4044 | 179.7882 | 179.8557 | 179.7753 | 179.9556 | 180.0084 | 180.0972 | 180.0584 | 180.2667 | 180.0546 | 179.9378 | 179.9173 | 180.0397 | 180.1243 | 181.3944 | 193.6756 | 227.1327 | 190.1938 | 190.5692 | 218.6134 | 235.9002 | 246.201 | 200.2263 | 201.4042 | 224.8914 | 241.9385 | 247.2265 | 252.1332 | 253.2833 | 255.2424 | 255.1288 | 255.0318 | 255.2733 | 254.9137 | 249.5272 | 236.4427 | 226.227 | 216.6706 | 204.337 | 218.502 | 212.7758 | 188.412 | 180.7656 | 180.0353 | 180.0876 | 180.2029 | 179.9767 | 180.0289 | 180.0856 | 184.6852 | 197.1486 | 199.7599 | 193.8068 | 207.4435 | 233.4764 | 239.0777 | 256.8739 | 262.1763 | 261.5471 | 257.8787 | 245.6696 | 261.0114 | 222.857 | 187.9277 | 180.2347 | 182.0033 | 186.3833 | 180.6457 | 180.4045 | 180.1044 | 179.7505 | 180.091 | 180.3163 | 180.2387 | 180.081 | 185.057
C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8985 | 52.8823 | 100.7679 | 267.4183 | 315.8571 | 317.0625 | 317.2828 | 316.8503 | 316.0959 | 316.7686 | 315.9028 | 312.6896 | 314.591 | 314.6784 | 313.1479 | 313.2213 | 313.5628 | 313.6747 | 312.7338 | 312.0967 | 311.4367 | 311.1354 | 310.6149 | 310.5223 | 310.0352 | 309.261 | 309.4645 | 310.8216 | 311.8458 | 315.1407 | 316.4836 | 316.844 | 317.2924 | 316.899 | 317.1829 | 316.6605 | 316.3295 | 316.6911 | 316.8552 | 316.7934 | 316.9784 | 316.8907 | 316.4646 | 316.7641 | 317.4126 | 317.8551 | 317.8697 | 317.9677 | 318.533 | 319.0925 | 318.6169 | 318.7478 | 319.0865 | 318.7121 | 318.4549 | 318.9088 | 319.252 | 319.4334 | 319.1615 | 319.3524 | 319.4469 | 320.7921 | 321.5765 | 322.2698 | 322.4057 | 321.9989 | 321.3438 | 320.1443 | 175.2114 | 26.9859 | 0 | 0
C4 | 260.1909 | 259.9022 | 259.767 | 259.8681 | 259.6049 | 260.0814 | 260.0607 | 259.8419 | 259.4928 | 259.8096 | 260.171 | 259.7345 | 259.9742 | 260.1759 | 259.9413 | 260.0264 | 259.9304 | 260.0243 | 260.1436 | 259.6961 | 260.2281 | 260.3166 | 280.9438 | 294.3626 | 293.3126 | 292.8679 | 295.4244 | 294.7956 | 295.6509 | 287.1187 | 259.9986 | 259.7758 | 259.7988 | 259.926 | 259.8731 | 260.4718 | 260.1534 | 260.0966 | 260.2641 | 259.8757 | 259.6986 | 260.274 | 260.3335 | 259.9192 | 260.1464 | 260.1405 | 259.7239 | 259.8949 | 259.9743 | 259.7006 | 260.2227 | 260.5315 | 260.1096 | 259.881 | 259.917 | 260.2333 | 259.9889 | 260.1287 | 259.8982 | 259.8972 | 260.0365 | 259.8031 | 259.4084 | 260.5054 | 259.9485 | 259.6035 | 259.5389 | 260.1588 | 259.7817 | 260.029 | 260.0652 | 259.8269 | 259.739 | 260.5013 | 259.8858 | 260.0125 | 259.5518 | 260.1464 | 259.2713 | 260.0286 | 260.1884 | 260.2073 | 259.5154 | 260.1947 | 260.2351 | 259.9419 | 260.1382 | 260.1874 | 260.1902 | 260.1736 | 259.7766 | 259.9953 | 260.1431 | 260.116 | 259.9907 | 259.9399
C5 | 180.3252 | 180.431 | 180.3853 | 180.4733 | 180.4026 | 180.549 | 180.4726 | 180.4552 | 180.5552 | 181.2546 | 181.0285 | 180.2299 | 180.4563 | 180.2033 | 180.4701 | 180.3752 | 180.2934 | 180.1631 | 180.0893 | 179.6132 | 179.8177 | 180.0641 | 180.2494 | 180.2389 | 180.1567 | 180.2757 | 180.5469 | 180.4003 | 180.7916 | 180.3314 | 180.3495 | 180.3331 | 180.6227 | 180.4242 | 180.9057 | 180.3302 | 198.1471 | 234.1401 | 255.5999 | 261.6285 | 260.1407 | 260.1143 | 255.498 | 259.9485 | 261.2547 | 261.0095 | 262.5144 | 262.5301 | 263.6133 | 269.2993 | 265.4207 | 263.6192 | 263.3462 | 262.7448 | 260.7611 | 260.0318 | 260.0278 | 260.3327 | 260.0993 | 261.2444 | 259.6723 | 259.3806 | 255.76 | 256.603 | 247.5139 | 238.3067 | 229.1217 | 230.6307 | 210.3018 | 207.7197 | 181.1815 | 181.0314 | 181.163 | 182.5154 | 182.789 | 183.3121 | 184.184 | 188.6538 | 187.0939 | 183.2085 | 183.8279 | 246.7589 | 259.3637 | 257.6554 | 238.4076 | 228.583 | 182.1527 | 181.3391 | 181.7221 | 180.8971 | 180.3764 | 180.2089 | 180.9669 | 181.6582 | 180.3934 | 186.6277
C6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.8041 | 64.406 | 207.489 | 324.1539 | 325.0405 | 307.0247 | 300.0802 | 300.1593 | 299.9721 | 300.0552 | 300.1648 | 300.1936 | 300.0916 | 299.9673 | 300.2056 | 300.0299 | 304.8139 | 315.2393 | 323.315 | 323.7571 | 323.184 | 316.2683 | 310.2556 | 299.974 | 300.1123 | 300.1018 | 300.0792 | 299.9322 | 300.2895 | 299.9301 | 299.8427 | 300.1028 | 299.9975 | 300.0611 | 299.8438 | 299.9753 | 300.032 | 300.0203 | 300.0003 | 300.1016 | 299.8778 | 299.8692 | 300.231 | 300.637 | 300.9865 | 321.9457 | 329.5322 | 329.6487 | 326.7927 | 304.7359 | 302.5306 | 300.1638 | 299.9922 | 300.4361 | 299.954 | 303.3266 | 305.7229 | 306.4864 | 300.2598 | 300.2779 | 300.0499 | 302.3242 | 305.3047 | 299.9551 | 140.3532
C7 | 261.3607 | 110.4528 | 12.4707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.794 | 77.7129 | 218.1618 | 307.6565 | 314.5402 | 292.2081 | 260.1492 | 259.5118 | 265.617 | 279.1274 | 263.0374 | 267.1862 | 264.473 | 266.1348 | 268.4106 | 264.3862 | 265.2769 | 264.7796 | 263.0691 | 268.325 | 267.1686 | 270.5469 | 274.5986 | 267.3619 | 265.3001 | 263.8363 | 263.7237 | 261.5277 | 261.3785 | 262.1491 | 261.4713 | 262.0535 | 262.6089 | 261.6298 | 261.2764 | 261.4359 | 261.435 | 261.0113 | 260.9533 | 260.9017 | 260.8242 | 261.2578 | 262.1495 | 262.3322 | 262.1801 | 262.1817 | 262.2629 | 263.7014 | 264.9716 | 265.7439 | 270.6787 | 270.3346 | 264.5555 | 264.4495 | 269.3719 | 261.3402 | 261.3899 | 262.9515 | 261.3496 | 261.851 | 262.7336 | 263.8926 | 261.9033 | 261.2787 | 260.8796 | 263.3015 | 262.8391 | 261.241 | 270.212
C8 | 300.1344 | 299.6011 | 212.1847 | 180.0621 | 180.096 | 180.1683 | 180.2092 | 180.1205 | 179.9364 | 180.0969 | 180.0321 | 179.8241 | 179.9516 | 179.8393 | 179.879 | 179.8392 | 179.8025 | 179.6329 | 179.6077 | 179.2591 | 179.1892 | 179.8615 | 179.9492 | 179.9089 | 179.9456 | 224.498 | 300.0068 | 253.6734 | 180.2344 | 179.8266 | 180.1039 | 179.9331 | 179.9978 | 180.1369 | 180.4435 | 179.9632 | 250.2317 | 339.1981 | 341.1628 | 342.0572 | 341.8854 | 343.0351 | 341.7359 | 342.5966 | 342.0367 | 340.6367 | 337.4648 | 339.6374 | 339.4237 | 340.9792 | 340.7714 | 341.4356 | 340.5319 | 338.552 | 339.826 | 340.6426 | 340.5755 | 340.6348 | 341.2618 | 341.0708 | 340.5788 | 340.7397 | 340.7374 | 340.666 | 340.4555 | 340.7158 | 340.5773 | 340.368 | 340.822 | 341.1229 | 341.4612 | 341.8172 | 341.8405 | 341.8884 | 342.0293 | 342.0507 | 342.0922 | 342.848 | 343.0532 | 343.5354 | 343.8237 | 343.8631 | 343.9178 | 343.9943 | 326.6404 | 299.9505 | 299.9468 | 299.9925 | 300.0172 | 299.9468 | 299.9488 | 299.9985 | 299.8783 | 300.077 | 299.9641 | 299.9046
Total load | 1362.0069 | 1222.8772 | 1027.0467 | 980.4379 | 980.2619 | 980.6663 | 980.5575 | 980.5206 | 979.8831 | 980.9014 | 980.9987 | 979.4836 | 980.4236 | 979.9191 | 980.0874 | 979.8292 | 979.9839 | 979.0672 | 979.5239 | 977.0079 | 977.7663 | 979.7768 | 1000.9218 | 1014.0547 | 1030.1282 | 1110.5058 | 1236.9167 | 1379.2184 | 1410.7545 | 1542.5854 | 1605.4361 | 1635.1775 | 1653.2486 | 1765.1452 | 1884.0884 | 1916.7777 | 2068.1031 | 2094.999 | 2123.4071 | 2183.4608 | 2217.0298 | 2243.9995 | 2141.8796 | 2146.1753 | 2191.9468 | 2224.5068 | 2238.0965 | 2252.6784 | 2268.7222 | 2290.9015 | 2280.7323 | 2278.6138 | 2270.0934 | 2264.0014 | 2241.3291 | 2214.495 | 2194.9922 | 2175.0898 | 2151.6298 | 2180.7986 | 2167.094 | 2116.7958 | 2097.4388 | 2096.1897 | 2086.1448 | 2076.4778 | 2066.614 | 2068.8068 | 2049.7395 | 2060.2426 | 2059.5382 | 2064.3755 | 2053.5982 | 2083.3025 | 2136.3993 | 2151.8276 | 2209.535 | 2238.1935 | 2235.7323 | 2216.2102 | 2171.3777 | 2269.5632 | 2191.7682 | 2120.9103 | 2069.2474 | 2035.5401 | 2004.5812 | 1993.678 | 1995.7473 | 1985.6348 | 1982.5858 | 1981.4699 | 1842.6427 | 1697.659 | 1661.607 | 1527.7061

## df_load_200804
| 0 | 1 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96
Load | 1362.0069 | 1222.8772 | 1027.0467 | 980.4379 | 980.2619 | 980.6663 | 980.5575 | 980.5206 | 979.8831 | 980.9014 | 980.9987 | 979.4836 | 980.4236 | 979.9191 | 980.0874 | 979.8292 | 979.9839 | 979.0672 | 979.5239 | 977.0079 | 977.7663 | 979.7768 | 1000.9218 | 1014.0547 | 1030.1282 | 1110.5058 | 1236.9167 | 1379.2184 | 1410.7545 | 1542.5854 | 1605.4361 | 1635.1775 | 1653.2486 | 1765.1452 | 1884.0884 | 1916.7777 | 2068.1031 | 2094.999 | 2123.4071 | 2183.4608 | 2217.0298 | 2243.9995 | 2141.8796 | 2146.1753 | 2191.9468 | 2224.5068 | 2238.0965 | 2252.6784 | 2268.7222 | 2290.9015 | 2280.7323 | 2278.6138 | 2270.0934 | 2264.0014 | 2241.3291 | 2214.495 | 2194.9922 | 2175.0898 | 2151.6298 | 2180.7986 | 2167.094 | 2116.7958 | 2097.4388 | 2096.1897 | 2086.1448 | 2076.4778 | 2066.614 | 2068.8068 | 2049.7395 | 2060.2426 | 2059.5382 | 2064.3755 | 2053.5982 | 2083.3025 | 2136.3993 | 2151.8276 | 2209.535 | 2238.1935 | 2235.7323 | 2216.2102 | 2171.3777 | 2269.5632 | 2191.7682 | 2120.9103 | 2069.2474 | 2035.5401 | 2004.5812 | 1993.678 | 1995.7473 | 1985.6348 | 1982.5858 | 1981.4699 | 1842.6427 | 1697.659 | 1661.607 | 1527.7061

## df_gen_200421
Unit | committable | p_min_pu | p_max_pu | marginal_cost | min_down_time | min_up_time | up_time_before | down_time_before | ramp_limit_up | ramp_limit_down | ramp_limit_start_up | ramp_limit_shut_down | shut_down_cost | start_up_cost | efficiency | p_nom | p_nom_min | p_nom_max
C1 | FALSE | 0.55 | 1 | 175 | 24 | 48 | 96 | 0 | 0.4 | 0.5 | 0 | 0.5 | 13000 | 18000 | 47.0752 | 340 | 300 | 340
C2 | FALSE | 0.53 | 1 | 175 | 24 | 48 | 96 | 0 | 0.4 | 0.5 | 0 | 0.5 | 13000 | 18000 | 48.7451 | 345 | 260 | 345
C3 | TRUE | 0.75 | 1 | 175 | 24 | 48 | 0 | 5 | 0.4 | 0.5 | 0.1 | 0.5 | 13000 | 18000 | 46.3336 | 325 | 50 | 325
C4 | TRUE | 0 | 1 | 175 | 24 | 48 | 0 | 3 | 0.4 | 0.5 | 0.1 | 0.5 | 13000 | 18000 | 44.7568 | 305 | 50 | 305
C5 | FALSE | 0.52 | 1 | 175 | 24 | 48 | 96 | 0 | 0.4 | 0.5 | 0 | 0.5 | 13000 | 18000 | 49.257 | 355 | 180 | 355
C6 | TRUE | 0 | 1 | 175 | 24 | 48 | 69 | 0 | 0.4 | 0.5 | 0.1 | 0.5 | 13000 | 18000 | 46.6806 | 345 | 50 | 345
C7 | FALSE | 0.76 | 1 | 175 | 24 | 48 | 0 | 96 | 0.4 | 0.5 | 0 | 0.5 | 13000 | 18000 | 0 | 0 | 0 | 0
C8 | TRUE | 0 | 1 | 175 | 24 | 48 | 72 | 0 | 0.4 | 0.5 | 0.1 | 0.5 | 13000 | 18000 | 47.2624 | 340 | 50 | 340

## load_200421
TIME | 0:00 | 0:15 | 0:30 | 0:45 | 1:00 | 1:15 | 1:30 | 1:45 | 2:00 | 2:15 | 2:30 | 2:45 | 3:00 | 3:15 | 3:30 | 3:45 | 4:00 | 4:15 | 4:30 | 4:45 | 5:00 | 5:15 | 5:30 | 5:45 | 6:00 | 6:15 | 6:30 | 6:45 | 7:00 | 7:15 | 7:30 | 7:45 | 8:00 | 8:15 | 8:30 | 8:45 | 9:00 | 9:15 | 9:30 | 9:45 | 10:00 | 10:15 | 10:30 | 10:45 | 11:00 | 11:15 | 11:30 | 11:45 | 12:00 | 12:15 | 12:30 | 12:45 | 13:00 | 13:15 | 13:30 | 13:45 | 14:00 | 14:15 | 14:30 | 14:45 | 15:00 | 15:15 | 15:30 | 15:45 | 16:00 | 16:15 | 16:30 | 16:45 | 17:00 | 17:15 | 17:30 | 17:45 | 18:00 | 18:15 | 18:30 | 18:45 | 19:00 | 19:15 | 19:30 | 19:45 | 20:00 | 20:15 | 20:30 | 20:45 | 21:00 | 21:15 | 21:30 | 21:45 | 22:00 | 22:15 | 22:30 | 22:45 | 23:00 | 23:15 | 23:30 | 23:45
C1 | 337.7177 | 338.3117 | 338.2401 | 338.4839 | 338.0183 | 338.3214 | 338.5876 | 338.4665 | 338.3767 | 338.4784 | 337.2643 | 338.2246 | 338.4383 | 337.8356 | 338.4475 | 338.4237 | 338.464 | 338.0515 | 339.161 | 338.6433 | 338.2132 | 338.9915 | 338.2525 | 322.088 | 337.4126 | 336.3017 | 335.1909 | 334.08 | 332.9692 | 331.8583 | 330.7475 | 329.6366 | 328.5258 | 327.4149 | 326.3041 | 325.1932 | 324.0824 | 322.9715 | 321.8607 | 320.7498 | 319.6389 | 318.5281 | 317.4848 | 319.385 | 320.2249 | 318.4605 | 315.7263 | 318.9171 | 316.8568 | 319.4424 | 318.8011 | 319.3549 | 320.3554 | 319.8929 | 317.9561 | 318.3382 | 319.7377 | 318.0916 | 316.6613 | 314.5125 | 316.273 | 316.8517 | 315.9341 | 323.5059 | 337.6088 | 338.4987 | 337.3674 | 329.7924 | 327.9943 | 329.4764 | 328.4711 | 326.5414 | 325.9994 | 327.0817 | 325.8912 | 326.0685 | 328.9863 | 328.8811 | 328.1077 | 328.1349 | 320.4924 | 320.2639 | 327.5475 | 327.9109 | 323.2212 | 328.6248 | 319.7206 | 320.1195 | 320.5183 | 320.9172 | 321.3161 | 321.7149 | 322.1138 | 322.5127 | 322.9115 | 323.3104
C2 | 305.317 | 339.1284 | 338.6417 | 334.1953 | 339.0424 | 339.1187 | 338.6375 | 338.4142 | 339.0785 | 338.8176 | 338.9464 | 338.3254 | 338.2653 | 338.8641 | 338.9378 | 338.9523 | 338.662 | 338.5059 | 338.5507 | 338.3894 | 338.7901 | 338.9564 | 339.0262 | 270.6472 | 292.3449 | 294.645 | 296.945 | 299.2451 | 301.5452 | 303.8453 | 306.1454 | 308.4454 | 310.7455 | 313.0456 | 315.3457 | 317.6458 | 319.9458 | 322.2459 | 324.546 | 326.8461 | 329.1461 | 331.4462 | 338.9047 | 339.7493 | 330.6382 | 338.9214 | 336.0595 | 339.803 | 337.487 | 339.5216 | 339.5167 | 339.4646 | 340.2953 | 339.5871 | 330.8007 | 339.2008 | 339.7218 | 338.9146 | 334.6207 | 334.5559 | 340.3421 | 332.7933 | 339.6024 | 339.3836 | 339.0213 | 339.0878 | 339.0081 | 339.308 | 338.2569 | 340.3092 | 337.7177 | 338.6224 | 338.5255 | 338.6324 | 338.7583 | 332.553 | 339.367 | 338.1581 | 338.4622 | 338.8686 | 335.3448 | 334.127 | 338.287 | 338.626 | 323.9808 | 339.4827 | 331.2113 | 330.4864 | 329.7615 | 329.0366 | 328.3117 | 327.5868 | 326.8619 | 326.137 | 325.4121 | 324.6872
C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.9243 | 73.6495 | 112.8374 | 312.1338 | 325.1036 | 324.561 | 324.0059 | 323.4507 | 322.8955 | 322.3403 | 321.7851 | 321.2299 | 320.6747 | 320.1195 | 319.5643 | 319.0091 | 318.4539 | 317.8987 | 317.3435 | 316.7883 | 316.2332 | 315.6779 | 312.3686 | 321.6922 | 281.068 | 275.261 | 266.6165 | 289.0526 | 320.8615 | 320.3453 | 320.9086 | 320.31 | 317.6508 | 316.0096 | 262.3755 | 299.6813 | 318.0234 | 317.489 | 319.4315 | 319.9291 | 317.9183 | 318.1239 | 319.8287 | 319.1179 | 319.6124 | 319.5175 | 321.9588 | 320.8084 | 320.1268 | 318.9425 | 321.6313 | 321.159 | 325.0815 | 321.9318 | 324.2954 | 317.9437 | 323.1001 | 323.1371 | 323.4687 | 324.8344 | 316.1306 | 301.0958 | 266.2516 | 278.5023 | 261.5232 | 322.8905 | 296.9461 | 297.5517 | 298.1573 | 298.7628 | 299.3684 | 299.974 | 300.5796 | 301.1851 | 301.7907 | 302.3963
C4 | 259.3962 | 29.0111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.5906 | 302.9521 | 303.2104 | 303.5279 | 302.3367 | 302.8741 | 302.354 | 301.8232 | 301.9938 | 301.7771 | 303.0316 | 300.301 | 303.2687 | 302.9522 | 301.5304 | 301.306 | 302.6734 | 303.4427 | 302.1112 | 303.0725 | 303.6497 | 303.245 | 302.671 | 303.5782 | 303.5696 | 303.6295 | 303.4453 | 303.3231 | 305.6232 | 304.9438 | 307.3505 | 306.7755 | 306.4419 | 306.4452 | 306.6699 | 307.2494 | 308.0739 | 308.0532 | 307.759 | 307.7816 | 307.9204 | 307.4628 | 308.839 | 308.4701 | 309.33 | 309.3607 | 309.3913 | 309.4219 | 309.4526 | 309.4832 | 309.5139 | 309.5445 | 309.5751 | 309.6057
C5 | 302.931 | 354.4069 | 354.8712 | 341.4834 | 352.2829 | 352.253 | 351.9867 | 352.6852 | 352.8392 | 352.7411 | 352.6399 | 352.6966 | 351.7339 | 352.6116 | 353.0974 | 353.1801 | 352.6484 | 352.4356 | 351.5124 | 352.4823 | 350.9721 | 350.8303 | 351.9664 | 299.2055 | 298.0244 | 301.2766 | 304.1443 | 307.012 | 309.8796 | 312.7473 | 315.615 | 318.4826 | 321.3503 | 324.2179 | 327.0856 | 329.9533 | 332.8209 | 335.6886 | 338.5562 | 341.4239 | 344.2916 | 347.1592 | 349.8526 | 349.8065 | 349.7384 | 347.8537 | 345.9468 | 348.2773 | 350.2233 | 349.6825 | 348.5753 | 347.1924 | 346.9413 | 346.738 | 337.6173 | 347.6883 | 347.437 | 346.2362 | 348.4766 | 347.6086 | 347.4304 | 345.0987 | 346.7921 | 349.1874 | 348.9811 | 349.3102 | 348.9487 | 350.5312 | 351.5573 | 350.5979 | 351.8433 | 351.0515 | 353.2319 | 353.3538 | 353.3463 | 351.2273 | 353.6934 | 353.4834 | 354.2142 | 354.0182 | 344.525 | 350.869 | 350.4273 | 354.0322 | 337.6544 | 354.4725 | 352.3176 | 351.2685 | 350.2194 | 349.1703 | 348.1213 | 347.0722 | 346.0231 | 344.974 | 343.925 | 342.8759
C6 | 339.761 | 339.6931 | 339.5269 | 260.9374 | 111.9951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1269 | 316.2022 | 310.6827 | 315.4086 | 312.6481 | 315.1205 | 313.6413 | 315.1892 | 315.2118 | 315.1177 | 315.5411 | 315.7341 | 314.9717 | 314.9094 | 316.3599 | 315.0369 | 315.2192 | 314.8531 | 315.2181 | 314.6273 | 315.4983 | 318.3614 | 338.1529 | 339.432 | 339.3775 | 326.6301 | 324.8595 | 326.0898 | 324.7995 | 325.2943 | 324.3093 | 324.9403 | 324.8939 | 320.4266 | 325.2912 | 324.9863 | 324.8069 | 324.9467 | 311.1567 | 315.8489 | 324.3336 | 324.6243 | 319.3721 | 324.6732 | 318.2516 | 318.6902 | 319.1288 | 319.5674 | 320.006 | 320.4446 | 320.8832 | 321.3218 | 321.7604 | 322.1989
C7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.9854 | 49.9409 | 65.8964 | 81.8519 | 97.8074 | 113.7629 | 129.7184 | 145.6739 | 161.6294 | 177.585 | 193.5405 | 209.496 | 225.4515 | 241.407 | 257.3625 | 273.318 | 289.2735 | 305.229 | 320.2148 | 321.637 | 321.276 | 320.514 | 321.7927 | 320.7925 | 318.5351 | 319.7371 | 320.4269 | 320.3604 | 320.6958 | 321.3012 | 319.8953 | 319.8793 | 321.865 | 319.9553 | 320.1416 | 319.8048 | 320.7015 | 320.3159 | 321.2112 | 320.0653 | 320.6115 | 319.9685 | 319.9109 | 321.972 | 319.8217 | 320.8239 | 320.1778 | 320.2681 | 320.1672 | 319.9305 | 319.8592 | 320.2619 | 319.7847 | 319.6221 | 320.1063 | 320.2546 | 319.8476 | 319.9666 | 320.076 | 320.2058 | 318.1851 | 320.1015 | 318.8898 | 319.5249 | 320.1599 | 320.7949 | 321.4299 | 322.0649 | 322.7 | 323.335 | 323.97 | 324.605
Total load | 1545.123 | 1400.5511 | 1371.2799 | 1275.1 | 1141.3386 | 1029.6932 | 1029.2118 | 1029.5659 | 1030.2943 | 1030.0371 | 1028.8505 | 1029.2466 | 1028.4375 | 1029.3113 | 1030.4827 | 1030.5561 | 1029.7744 | 1028.993 | 1029.2241 | 1029.515 | 1051.8997 | 1102.4278 | 1142.0826 | 1204.0745 | 1286.8708 | 1306.7252 | 1326.1824 | 1345.6397 | 1365.0969 | 1384.5541 | 1404.0113 | 1423.4685 | 1442.9257 | 1462.3829 | 1481.8401 | 1501.2973 | 1520.7545 | 1540.2117 | 1559.6689 | 1579.1261 | 1598.5833 | 1618.0406 | 2251.543 | 2271.4243 | 2216.8387 | 2219.9472 | 2201.1266 | 2234.8371 | 2259.959 | 2265.7412 | 2265.4341 | 2263.5771 | 2264.5114 | 2259.564 | 2186.8853 | 2242.6495 | 2264.6752 | 2257.0296 | 2257.2244 | 2254.7068 | 2259.9946 | 2250.8833 | 2262.5165 | 2272.8666 | 2306.6589 | 2309.3929 | 2310.141 | 2292.6717 | 2286.0617 | 2289.5628 | 2290.2639 | 2287.8806 | 2294.6652 | 2292.6459 | 2293.4861 | 2274.9261 | 2296.8926 | 2295.5173 | 2297.2399 | 2299.1107 | 2255.2561 | 2249.9529 | 2234.8434 | 2251.3643 | 2192.7758 | 2298.7153 | 2246.6671 | 2247.0018 | 2247.3365 | 2247.6712 | 2248.006 | 2248.3406 | 2248.6754 | 2249.01 | 2249.3448 | 2249.6794

## df_load_200421
| 0 | 1 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96
Load | 1545.123 | 1400.5511 | 1371.2799 | 1275.1 | 1141.3386 | 1029.6932 | 1029.2118 | 1029.5659 | 1030.2943 | 1030.0371 | 1028.8505 | 1029.2466 | 1028.4375 | 1029.3113 | 1030.4827 | 1030.5561 | 1029.7744 | 1028.993 | 1029.2241 | 1029.515 | 1051.8997 | 1102.4278 | 1142.0826 | 1204.0745 | 1286.8708 | 1306.7252 | 1326.1824 | 1345.6397 | 1365.0969 | 1384.5541 | 1404.0113 | 1423.4685 | 1442.9257 | 1462.3829 | 1481.8401 | 1501.2973 | 1520.7545 | 1540.2117 | 1559.6689 | 1579.1261 | 1598.5833 | 1618.0406 | 2251.543 | 2271.4243 | 2216.8387 | 2219.9472 | 2201.1266 | 2234.8371 | 2259.959 | 2265.7412 | 2265.4341 | 2263.5771 | 2264.5114 | 2259.564 | 2186.8853 | 2242.6495 | 2264.6752 | 2257.0296 | 2257.2244 | 2254.7068 | 2259.9946 | 2250.8833 | 2262.5165 | 2272.8666 | 2306.6589 | 2309.3929 | 2310.141 | 2292.6717 | 2286.0617 | 2289.5628 | 2290.2639 | 2287.8806 | 2294.6652 | 2292.6459 | 2293.4861 | 2274.9261 | 2296.8926 | 2295.5173 | 2297.2399 | 2299.1107 | 2255.2561 | 2249.9529 | 2234.8434 | 2251.3643 | 2192.7758 | 2298.7153 | 2246.6671 | 2247.0018 | 2247.3365 | 2247.6712 | 2248.006 | 2248.3406 | 2248.6754 | 2249.01 | 2249.3448 | 2249.6794

## Parameters
attribute | type | unit | default | description | status
name | string | n/a | n/a | Unique name | Input (required)
bus | string | n/a | n/a | name of bus to which generator is attached | Input (required)
control | string | n/a | PQ | P,Q,V control strategy for PF, must be “PQ”, “PV” or “Slack”. | Input (optional)
type | string | n/a | n/a | Placeholder for generator type. Not yet implemented. | Input (optional)
p_nom | float | MW |  | Nominal power for limits in OPF. | Input (optional)
p_nom_extendable | boolean | n/a | FALSE | Switch to allow capacity p_nom to be extended in OPF. | Input (optional)
p_nom_min | float | MW |  | If p_nom is extendable in OPF, set its minimum value. | Input (optional)
p_nom_max | float | MW | inf | If p_nom is extendable in OPF, set its maximum value (e.g. limited by technical potential). | Input (optional)
p_min_pu | static or series | per unit |  | The minimum output for each snapshot per unit of p_nom for the OPF (e.g. for variable renewable generators this can change due to weather conditions and compulsory feed-in; for conventional generators it represents a minimal dispatch). Note that if comittable is False and p_min_pu > 0, this represents a must-run condition. | Input (optional)
p_max_pu | static or series | per unit |  | The maximum output for each snapshot per unit of p_nom for the OPF (e.g. for variable renewable generators this can change due to weather conditions; for conventional generators it represents a maximum dispatch). | Input (optional)
p_set | static or series | MW |  | active power set point (for PF) | Input (optional)
q_set | static or series | MVar |  | reactive power set point (for PF) | Input (optional)
sign | float | n/a |  | power sign | Input (optional)
carrier | string | n/a | n/a | Prime mover energy carrier (e.g. coal, gas, wind, solar); required for global constraints on primary energy in OPF | Input (optional)
marginal_cost | static or series | currency/MWh |  | Marginal cost of production of 1 MWh. | Input (optional)
capital_cost | float | currency/MW |  | Capital cost of extending p_nom by 1 MW. | Input (optional)
efficiency | float | per unit |  | Ratio between primary energy and electrical energy, e.g. takes value 0.4 MWh_elec/MWh_thermal for gas. This is required for global constraints on primary energy in OPF. | Input (optional)
committable | boolean | n/a | FALSE | Use unit commitment (only possible if p_nom is not extendable). | Input (optional)
start_up_cost | float | currency |  | Cost to start up the generator. Only read if committable is True. | Input (optional)
shut_down_cost | float | currency |  | Cost to shut down the generator. Only read if committable is True. | Input (optional)
min_up_time | int | snapshots | 0 | Minimum number of snapshots for status to be 1. Only read if committable is True. | Input (optional)
min_down_time | int | snapshots | 0 | Minimum number of snapshots for status to be 0. Only read if committable is True. | Input (optional)
up_time_before | int | snapshots | 1 | Number of snapshots that the generator was online before network.snapshots start. Only read if committable is True and min_up_time is non-zero. | Input (optional)
down_time_before | int | snapshots | 0 | Number of snapshots that the generator was online before network.snapshots start. Only read if committable is True and min_down_time is non-zero. | Input (optional)
ramp_limit_up | float | per unit | NaN | Maximum active power increase from one snapshot to the next, per unit of the nominal power. Ignored if NaN. | Input (optional)
ramp_limit_down | float | per unit | NaN | Maximum active power decrease from one snapshot to the next, per unit of the nominal power. Ignored if NaN. | Input (optional)
ramp_limit_start_up | float | per unit |  | Maximum active power increase at start up, per unit of the nominal power. Only read if committable is True. | Input (optional)
ramp_limit_shut_down | float | per unit |  | Maximum active power decrease at shut down, per unit of the nominal power. Only read if committable is True. | Input (optional)
p | series | MW |  | active power at bus (positive if net generation) | Output
q | series | MVar |  | reactive power (positive if net generation) | Output
p_nom_opt | float | MW |  | Optimised nominal power. | Output
status | series | n/a | 1 | Status (1 is on, 0 is off). Only outputted if committable is True. | Output
mu_upper | series | currency/MWh |  | Shadow price of upper p_nom limit | Output
mu_lower | series | currency/MWh |  | Shadow price of lower p_nom limit | Output
mu_p_set | series | currency/MWh |  | Shadow price of fixed power generation p_set | Output
mu_ramp_limit_up | series | currency/MWh |  | Shadow price of upper ramp up limit | Output
mu_ramp_limit_down | series | currency/MWh |  | Shadow price of lower ramp down limit | Output
generator.{p_nom, p_nom_extendable, p_nom_min, p_nom_max, p_min_pu, p_max_pu, marginal_cost, capital_cost, efficiency, carrier}